## Genset
GENSET
Daily
Column Header (ID) | Type | Enum Options / Values | Hint / Display Name
Check Date | Date | TODAY() | Date of Inspection
Genset Unit | Ref | (Link to your Inventory Table) | Select Unit (e.g., Well 4 BAR)
Fuel Level | Enum | Full, 75%, 50%, Low | Fuel Tank Status
Oil Level | Enum | Normal, Low, Overfilled | Engine Oil Level
Coolant Level | Enum | Normal, Low | Coolant Level
Battery Condition | Enum | Clean, Corroded, Loose | Battery Terminals
Air Intake | Enum | Clear, Restricted | Air Intake Status
Control Panel | Enum | No Alarms, Active Alarm | Panel Status
Louver Status | Enum | Clear, Obstructed | Enclosure/Louver Opening
Technician Sign | Signature | - | Signature of Inspector
Weekly
Column Header | Type | Enum Options / Values | Input Mode
Weekly Date | Date | TODAY() | Auto
Genset ID | Ref | (Link to Inventory) | Dropdown
Battery Charger | Enum | Charging, Floating, Off | Buttons
Drive Belts | Enum | Tight, Loose, Cracked | Buttons
Radiator Hoses | Enum | Flexible, Hard/Brittle, Leaking | Buttons
Water Separator | Enum | Drained, Clean, Contaminated | Buttons
Block Heater | Enum | Warm, Cold, Not Installed | Buttons
Exhaust System | Enum | Sealed, Soot Visible, Damaged | Buttons
Monthly
Column Header | Type | Enum Options / Values | Input Mode
Monthly Date | Date | TODAY() | Auto
Genset ID | Ref | (Link to Inventory) | Dropdown
No Load Run | Enum | Pass (15-30m), Failed, Did Not Start | Buttons
Battery Fluid | Enum | Level OK, Topped Up, Low | Buttons
Main Breaker | Enum | Functional, Stiff/Stuck | Buttons
Control Wiring | Enum | Secure, Frayed, Loose | Buttons
Flexible Lines | Enum | Good Condition, Seeping | Buttons
Engine Hours | Number | (Manual Input for Hour Meter) | Stack
Quarterly
Column Header | Type | Enum Options / Values | Input Mode
Quarterly Date | Date | TODAY() | Auto
Genset ID | Ref | (Link to Inventory) | Dropdown
Air Filter Elem | Enum | Clean, Dirty (Replace), Replaced | Buttons
Radiator Cleaning | Enum | Clean/Clear, Dust Clogged, Flushed | Buttons
Alternator Screen | Enum | No Obstruction, Cleaned Dust | Buttons
Linkage Lubrication | Enum | Lubricated, Stiff/Dry | Buttons
Yearly
Column Header | Type | Enum Options / Values | Input Mode
Yearly Date | Date | TODAY() | Auto
Genset ID | Ref | (Link to Inventory) | Dropdown
Oil Filter Change | Enum | Completed, Not Due | Buttons
Engine Oil Change | Enum | Completed, Not Due | Buttons
Fuel Filter Change | Enum | Completed, Not Due | Buttons
Coolant DCA Test | Enum | Pass, Fail (Add SCA), Replace | Buttons
Breather Cleaning | Enum | Cleaned, Replaced | Buttons
ATS Inspection | Enum | Contacts Clean, Pitting Seen | Buttons
Load Bank Test | Enum | Pass, Fail, Not Required | Buttons

## RO
RO
Daily
Weekly
Column Header | Type | Enum Options / Values | Hint
Conductivity Probe | Enum | Calibrated, Cleaned, Needs Replace | Verify TDS Meter Accuracy
Low Pressure Cutoff | Enum | Tested/Passed, Failed | Safety Trip for High Pressure Pump
High Pressure Trip | Enum | Tested/Passed, Failed | Overpressure Protection
Permeate Check Valve | Enum | Sealing, Backflowing | Prevent back-pressure on membranes
Monthly
Column Header | Type | Enum Options / Values | Hint
Normalized Flow | Enum | Stable, Dropped >10%, Dropped >15% | Calculate flow vs. startup data
Vessel Racks | Enum | Secure, Rusting, Loose Bolts | Inspect Steel Support Frames
Victaulic Couplings | Enum | Tight, Salt Creep Visible | Check for corrosion at joints
Membrane Autopsy | Enum | Not Required, Visual Check Done | Check lead membrane for fouling
Quarterly
Column Header | Type | Enum Options / Values | Hint
CIP Procedure | Enum | Performed (Acid/Alkaline), Skipped | Clean-In-Place Service
Vessel O Rings | Enum | Replaced, Lubricated, Good | End-cap seal maintenance
Interconnectors | Enum | Inspected, Replaced O-rings | Internal membrane connectors
Membrane Rotation | Enum | Completed, Not Required | Moving tail elements to lead (if applicable)
Pressure Gauges | Enum | Re-calibrated, Replaced | Ensure all PSI readings are true

## Dosing Pump
GENSET
Daily
Column Header | Type | Enum Options / Values | Hint | d
Check_Time | DateTime | NOW() | Auto-timestamp
Pump_ID | Ref | (Link to Pump Inventory) | Select Dosing Pump
Priming_Status | Enum | Primed, Air-Locked, Loss of Prime | Is there air in the head?
Diaphragm_Click | Enum | Regular, Irregular, Silent | Listen for the mechanical stroke
Chemical_Level | Number | (Manual Input in Liters/%) | Current tank level
Injection_Point | Enum | Clear, Calcified/Blocked | Check the nozzle at the pipe |  | Daily
Leak_Check | Enum | Dry, Seeping, Active Leak | Check the pump head and fittings |  | Weekly
Weekly |  |  |  |  | Monthly
Column Header | Type | Enum Options / Values | Hint | w | Quarterly
Drawdown_Test | Enum | Accurate, Over-Dosing, Under-Dosing | Use a calibration cylinder |  | Yearly
Suction_Strainer | Enum | Clean, Clogged, Sludge Visible | Check the foot valve in the tank
Tubing_Condition | Enum | Flexible, Brittle, Discolored | Check discharge/suction lines
Vent_Valve | Enum | Functional, Clogged | Check the manual bleed valve
Monthly
Column Header | Type | Enum Options / Values | Hint | m
Stroke_Adjustment | Enum | Moves Freely, Stuck, Hard to Turn | Check the manual stroke knob
Electrical_Plug | Enum | Secure, Corrosion on Pins | Check for chemical fumes damage
Controller_Sync | Enum | Running, External Stop Active | Check if RO/Well signal is on
Mounting_Bolts | Enum | Tight, Loose/Vibrating | Check the shelf or tank mount
Yearly
Column Header | Type | Enum Options / Values | Hint | q/Y
Diaphragm_Swap | Enum | Replaced, Inspected OK | Preventive change (Annual)
Check_Valves | Enum | Replaced, Cleaned | Ball and seat replacement
O_Rings | Enum | Replaced, Lubricated | Prevent air leaks
Backpressure_Valve | Enum | Tested, Failed/Replaced | Ensure consistent dosing

## Controllers
GENSET
Weekly
Column Header | Type | Enum Options / Values | Hint
Check Time | DateTime | NOW() | Auto-timestamp
Controller ID | Ref | (Link to Inventory) | Select VFD/Softstarter
Running Frequency | Number | (Manual Input in Hz) | Current output (for VFDs)
Operating Amps | Number | (Manual Input in Amperes) | Check against motor FLA
Heatsink Temp | Number | (Manual Input in °C) | Check via internal display
Cooling Fans | Enum | Spinning, Making Noise, Stopped | Check airflow |  | Daily
Fault Codes | Enum | None, Active Fault, Warning | Check display for errors |  | Weekly
Panel Humidity | Enum | Dry, Condensation Visible | Check for moisture |  | Monthly
Monthly |  |  |  |  | Quarterly
Column Header | Type | Enum Options / Values | Hint |  | Yearly
Panel Filters | Enum | Clean, Dust Clogged, Replaced | Wash or replace air filters
Louver Vents | Enum | Clear, Obstructed | Ensure heat can escape
External Vibration | Enum | Stable, Excessive | Check for nearby machinery vibration
Display Visibility | Enum | Clear, Faded/Flickering | Ensure screen is readable
Quarterly
Column Header | Type | Enum Options / Values | Hint
Internal Dust | Enum | None, Light, Heavy (Vacuumed) | Use vacuum, not compressed air
Terminal Discolor | Enum | Normal, Signs of Overheating | Check for burnt/darkened wires
Cable Integrity | Enum | Secure, Loose, Rodent Damage | Inspect input/output power lines
Ground Connection | Enum | Tight/Clean, Corroded | Essential for VFD safety
Yearly
Column Header | Type | Enum Options / Values | Hint | q/y
Terminal Torque | Enum | Checked/Tightened, Loose | Re-torque all power terminals
Capacitor Check | Enum | No Bulging, Leaking, Good | Visual check of DC bus capacitors
Fan Replacement | Enum | Operational, Replaced | Fans usually last 3-5 years
Backup Parameters | Enum | Uploaded to Cloud, Not Done | Save settings via software/USB
Heatsink Cleaning | Enum | Deep Cleaned, No Blockage | Ensure fins are totally clear
[5 empty] | Column Header | Check Time | Controller ID | Running Frequency | Operating Amps | Heatsink Temp | Cooling Fans | Fault Codes | Panel Humidity | Panel Filters | Louver Vents | External Vibration | Display Visibility | Internal Dust | Terminal Discolor | Cable Integrity | Ground Connection | Terminal Torque | Capacitor Check | Fan Replacement | Backup Parameters | Heatsink Cleaning
[5 empty] | Type | DateTime | Ref | Number | Number | Number | Enum | Enum | Enum | Enum | Enum | Enum | Enum | Enum | Enum | Enum | Enum | Enum | Enum | Enum | Enum | Enum
[5 empty] | Enum Options / Values | NOW() | (Link to Inventory) | (Manual Input in Hz) | (Manual Input in Amperes) | (Manual Input in °C) | Spinning, Making Noise, Stopped | None, Active Fault, Warning | Dry, Condensation Visible | Clean, Dust Clogged, Replaced | Clear, Obstructed | Stable, Excessive | Clear, Faded/Flickering | None, Light, Heavy (Vacuumed) | Normal, Signs of Overheating | Secure, Loose, Rodent Damage | Tight/Clean, Corroded | Checked/Tightened, Loose | No Bulging, Leaking, Good | Operational, Replaced | Uploaded to Cloud, Not Done | Deep Cleaned, No Blockage
[5 empty] | Hint | Auto-timestamp | Select VFD/Softstarter | Current output (for VFDs) | Check against motor FLA | Check via internal display | Check airflow | Check display for errors | Check for moisture | Wash or replace air filters | Ensure heat can escape | Check for nearby machinery vibration | Ensure screen is readable | Use vacuum, not compressed air | Check for burnt/darkened wires | Inspect input/output power lines | Essential for VFD safety | Re-torque all power terminals | Visual check of DC bus capacitors | Fans usually last 3-5 years | Save settings via software/USB | Ensure fins are totally clear

## Cartridge Filter
GENSET
Daily
Column Header | Type | Enum Options / Values | Hint
Check_Time | DateTime | NOW() | Auto-timestamp
Housing_Leaks | Enum | None, Cover Leak, Drain Leak | Check body and seals
Visual_Clarity | Enum | Clear, Cloudy, Sediment Noted | Check downstream sample (if available)
Weekly |  |  |  |  | Daily
Column Header | Type | Enum Options / Values | Hint |  | Weekly
Pressure_Gauges | Enum | Working, Stuck, Fogged/Broken | Ensure readings are reliable |  | Monthly
Housing_Vents | Enum | Air Bled, Functional | Ensure no air is trapped in the top |  | Quarterly
Drain_Valve | Enum | Closed/Dry, Seeping | Check the bottom flush valve |  | Yearly
Mounting_Support | Enum | Stable, Vibrating, Loose | Check housing legs/brackets
Monthly
Column Header | Type | Enum Options / Values | Hint
Filter_Condition | Enum | New, Slightly Discolored, Dark/Slimy | Visual check of the element
Internal_O_Ring | Enum | Elastic, Flattened, Nicked | Check the main housing seal
Spring_Plate | Enum | Secure, Rusting, Missing | Check top compression plate
Replacement_Done | Enum | No, Element Replaced | Record if a new filter was installed
Quarterly
Column Header | Type | Enum Options / Values | Hint | q/y
Housing_Sanitize | Enum | Completed, Not Required | Clean inside housing with mild bleach
Gauge_Calibration | Enum | Calibrated, Replaced | Ensure $\Delta P$ is mathematically true
Support_Pipe_Inspect | Enum | Good, Corrosion Noted, Leaking | Check connection to main RO line
Stock_Level_Check | Enum | >5 Spares, <2 Spares (Order!) | Inventory management for elements

## Pump and Motor
GENSET
Daily
Column Header | Type | Enum Options / Values | Hint / Logic
Check Time | DateTime | NOW() | Auto-timestamp
Asset ID | Ref | (Link to Inventory) | Select Pump/Motor
Vibration Level | Enum | Smooth, Slight, Excessive | Feel the motor frame
Operating Temp | Enum | Normal/Warm, Hot to Touch | Check housing temperature
Seal Leakage | Enum | None, Occasional Drip, Active Leak | Check the mechanical seal
Abnormal Noise | Enum | None, Grinding, Squealing | Listen for bearing wear
Discharge PSI | Number | (Manual Input) | Check the pressure gauge
Weekly
Column Header | Type | Enum Options / Values | Hint
Amperage Draw | Number | (Manual Input) | Verify against nameplate FLA
Mounting Bolts | Enum | Tight, Loose/Vibrating | Check the baseplate/foundation
Coupling Guard | Enum | Secure, Missing, Rubbing | Safety check for rotating parts | Daily
Oil Level Sight | Enum | Full, Low, Discolored/Milky | For oil-lubricated bearings | Weekly
Monthly |  |  |  | Monthly
Column Header | Type | Enum Options / Values | Hint | Quarterly
Grease Applied | Enum | Yes (1-2 Pumps), Not Required | Do not over-grease! | Yearly
Terminal Box | Enum | Clean/Dry, Moisture/Dust Found | Open the motor junction box
Cooling Fins | Enum | Clean, Clogged with Dust | Blow out motor air channels
Suction Strainer | Enum | Clear, Partially Blocked | Check inlet for debris
Quarterly
Column Header | Type | Enum Options / Values | Hint
Shaft Alignment | Enum | Aligned, Misaligned | Check coupling gap/parallelism
Insulation Test | Number | (Manual Input in MΩ) | Megger test for motor windings
Flow Rate Check | Number | (Manual Input) | Compare GPM to pump curve
Bearing Temp IR | Number | (Manual Input in °C) | Use IR thermometer on bearings
Yearly
Column Header | Type | Enum Options / Values | Hint
Mechanical Seal | Enum | Replaced, Inspected OK | Preventive seal kit swap
Bearing Swap | Enum | Replaced, Inspected OK | Listen for "roughness"
Coupling Insert | Enum | Replaced Spider, Good | Check for wear in flexible coupling
Paint Touchup | Enum | Completed, No Corrosion | Prevent rust on the pump volute

## Quality Tester
Hint / Instruction
Submerge in 800ppm or 1000ppm standard. If reading is >2% off, recalibrate.
Rinse with distilled water after every use to prevent salt buildup on the pins.
Check the battery indicator. Low voltage causes "flickering" or erratic readings.
Place in high-quality distilled water. Reading should be 0–2 ppm.
Inspect the battery compartment and screen for signs of water or chemical ingress.
Inspect the metal electrodes inside the probe. If pitted or rusted, the unit must be replaced.
Upload the certificate of calibration if the unit was sent to a lab or 3rd party.
pH Meter
| Frequency | Column Header | Type | Enum Options / Values | Hint / Instruction
| Daily | Storage Check | Enum | Wet (KCL), Dry (Action Required), Refilled | Ensure the sensor cap contains KCL storage solution. Never store in distilled water.
| Weekly | pH 7 Buffer Calib | Enum | Passed (7.0), Adjusted, Failed | Dip in pH 7.00 buffer. This sets the "Zero Point" of the meter.
| Weekly | pH 4 10 Slope Calib | Enum | Passed (4.0/10.0), Adjusted, Failed | Dip in a second buffer (usually 4.0 for acidic or 10.0 for basic water) to set the slope.
| Monthly | Electrode Cleaning | Enum | Cleaned (Acid Soak), Good, Scaling Removed | Soak the glass bulb in a cleaning solution or 0.1M HCl to remove mineral buildup.
| Monthly | Response Time | Enum | Fast (<30s), Slow (Sluggish), Critical (>60s) | Record how long the reading takes to stabilize. Slow response means the probe is aging.
| Quarterly | Junction Inspect | Enum | Clear, Clogged (Salt), Discolored | Inspect the reference junction (small white/ceramic dot) for clogs or "poisoning."
| Yearly | Probe Replacement | Enum | Replaced, Still Functional | Most pH electrodes lose accuracy after 12–18 months. Replace if calibration fails.
NTU Meter
| Frequency | Column Header | Type | Enum Options / Values | Hint / Instruction
| Weekly | Vial Clarity Check | Enum | Clean/Clear, Smudged (Cleaned), Scratched | Wipe the outside of the glass vial with a lint-free cloth and a drop of silicone oil.
| Weekly | Zero Standard Verify | Enum | Passed (<0.1 NTU), High (Re-zeroed) | Insert the 0.02 NTU (or 0.00) standard. Ensure the reading is within ±0.05 NTU.
| Monthly | Secondary Std Check | Enum | Matched (10/100 NTU), Drifted | Check against the 10 NTU or 100 NTU Gelex standards to verify the sensor's slope.
| Monthly | Chamber Cleaning | Enum | No Dust, Cleaned (Air/Q-tip) | Use a dry Q-tip or air blower to remove dust from the internal optical chamber.
| Quarterly | Vial Replacement | Enum | Good Condition, Replaced (New) | Inspect vials under a bright light. If micro-scratches are visible, discard the vial.
| Yearly | Light Source Audit | Enum | Stable, Flickering (Repair) | Check the lamp strength. If the reading fluctuates wildly with a standard, the lamp is failing.
| Yearly | Formazin Calib | File | (Upload PDF Certificate) | Perform a full calibration using fresh Formazin primary standards or send for ISO certification.
Colorometer
| Frequency | Column Header | Type | Enum Options / Values | Hint / Instruction
| Weekly | Blanking Verification | Enum | Zeroed (0.00), High (Re-zeroed) | Always "Zero" the meter using the raw water sample before adding DPD.
| Weekly | Reagent Check | Enum | In-Stock, Expired, Low Stock | Check the DPD powder/tablets. Expired reagents cause false "Low" readings.
| Monthly | Optical Cell Clean | Enum | Clean, Dust Found (Cleaned) | Use a dry Q-tip to clean the internal chamber. Fingerprints here block the light.
| Monthly | Vial Match Check | Enum | Matched, Scratched (Discarded) | Use the same vial for "Zero" and "Sample" to avoid glass-thickness errors.
| Quarterly | Secondary Std Test | Enum | Passed (0.2/1.0/2.0), Calibrated | Use "Spec-Check" colored gel standards to verify the meter's linearity.
| Yearly | Comparison Audit | Enum | Matched (Titration), Discrepancy | Compare digital results with a DPD Titration kit or a 3rd party lab test.
| Yearly | Battery Compartment | Enum | Clean/Dry, Corrosion Noted | Inspect for chemical fumes or battery leaks that damage the internal circuits.